## 3T scoring
Spec Section | Description | Status | Requirement | Yes | No | Bidder Response | Bidder Cross Reference
| Department of National Defence (DND), 1st Canadian Air Division, Winnipeg, Manitoba has a requirement for the lease of one (1) Mobile Aircraft Rescue and Fire Fighting Simulator (MARFFS) as per the detailed mandatory specifications attached herein. The period of the lease will be for a three (3) year period from date of award. Delivery of the unit will be to CFB Greenwood, Nova Scotia. STATUS : M=Mandatory; I = Information |  | Note: It’s a mandatory requirement that the bidder fill out the Compliance Matrix and meets all of the mandatory specifications as identified under herein. Failure to meet the mandatory requirements addressed in this Compliance Matrix will result in your proposal being deemed non-responsive and it shall not be given any further consideration in the evaluation process. Bidders MUST provide documentation of the (MARFFS) and should cross reference where each of the Mandatories below can be found within the documentation.
1 | Part 1: Overview
1.01 | A need exists to provide realistic, environmentally friendly Aircraft Rescue and Fire Fighting (ARFF) training to Canadian Forces (CF) military firefighters. ARFF training must be conducted in accordance with the North Atlantic Treaty Organization (NATO) STANAG 7145. Which calls for, in part, several ARFF training opportunities throughout a given year. | I
1.02 | An ARFF simulator is required that will provide CF firefighters a system that is highly mobile and can be a designated training aid for several Bases or Wings. The simulator must be ruggedly designed, environmental approved, and easily assembled/disassembled by local firefighters. | I
1.03 | The simulator must be a product already successfully in use by United States Air Force (USAF) and NATO countries. | M
2 | Part 2: MARFFS Training Capabilities
2.01 | Engine Fires: The simulator must provide realistic aircraft engine fire scenarios. | M
2.02 | Wing Fires: The simulator must provide aircraft wing fire scenarios. | M
2.03 | Cock Pit Fires: The simulator must provide partially and fully engulfed scenarios required. | M
2,04 | Cargo Hold Fires: The simulator must provide partially or fully engulfed scenarios required. | M
2.05 | Aircraft Wheel Fires: The simulator must provide aircraft wheel fires. | M
2.06 | Auxiliary Power Unit (APU) fires: The simulator must provide realistic pressurized APU fires. | M
2.07 | Fuel Leaks: The simulator must produce large scale aircraft fuel leak scenarios. | M
2.08 | Battery Over Heat/Fires: The simulator must provide aircraft overheated battery or fire scenarios. | M
2.09 | 3-Dimensional Fires: The simulator must provide 3-D fire scenarios. | M
2.11 | Aircraft Ramp Door: Must be fully functional and manually open and close as a training scenario will call for. | M
2.12 | Crew/Passenger Door: Must be fully functional to open and close. | M
2.13 | Set-Up: The simulator must be prepared within 2-3 hours by a maximum of two (2) firefighters.. | M
3 | Part 3: MARFFS Size Requirements
3.01 | Weight: Must not weigh more than 32,000 lbs. | M
3.02 | Mobile Configuration: Must be no greater than 45' long x 13' high x 8.5' wide. Must be legally capable of being transported on Canadian highways in this configuration. | M
4 | Part 4: MARFFS Mobility
4.01 | Removable components for operations and training must be transportable using only the vehicle and aircraft mockup. | M
4.02 | The removable components must not exceed 100 lbs in weight. | M
4.03 | The mobile aircraft fire trainer must be equipped with the means to secure all components during transport. | M
4.04 | The mobile aircraft fire trainer must meet all Canadian Transportation requirements for commercial vehicles without waivers for size and weight restrictions. | M
4.05 | Special Tools: The mobile aircraft fire trainer must not require special tools or equipment for maintenance, setup, or operation. All repair parts shall be commercially available. | M
5 | Part 5: Safety Systems
5.01a | Basic Features: The system must continuously monitor the following: - Computer activity - The position of safety propane valves - The presence of a pilot flame - The presence of main flames - The presence of smoke generation - Trainer propane levels - Compartment temperature levels - The positions of all emergency stop switches. | M
5.01b | Basic Features: If an unsafe condition occurs, the computer must shut off the following: - Electrical power to all fires - Stop the distribution of propane - Stop smoke generation, and turn on the ventilation system. The ventilation system shall remain on until 30 seconds after being manually reset. The emergency shutdown condition must be reported to the operator. | M
5.02 | Minimum Safety Features: The trainer must incorporate the following safety features (as a minimum) into the basic system: a) Propane vapor system monitoring b) Training compartment temperature monitoring c) Pilot flame status monitoring d) Hardware malfunction detection e) Exhaust ventilation system and monitoring f) Combustion air system and monitoring g) Emergency shutdown system h) Propane vapor pressure monitoring i) Power loss automatic shutdown | M
5.03 | Propane System Monitoring: The air within the training compartment must be continuously monitored at two (2) different locations for any concentrations of unburned gases. | M
5.04 | The air space must be analyzed for unburned combustible gas content in order to detect any buildup of gas in the training compartment before dangerous levels are reached. | M
5.05 | The combustible gas concentration levels must be constantly reported to the system, and measured as a percent of the Lower Explosive Level (LEL). | M
5.06 | Should the detected gas concentration level at either location reach 10% LEL, the compartment exhaust fan must be automatically turned on and purge the compartment of gas before dangerous levels are reached. | M
5.07 | Should the detected gas concentration level at either location reach 25% LEL, an automatic and immediate shutdown of the entire trainer must occur and the exhaust fan must continue to operate and the gas supply to the trainer must be turned off and disabled. | M
5.08 | Temperature Monitoring: The thermocouple must be mounted between 4'-5' from the floor. | M
5.09 | Temperature Monitoring: If the thermocouple detects a temperature level greater than 500 degrees F, the ventilation fan must ramp up until the level falls below 500 degrees F. | M
5.1 | Temperature Monitoring: If the temperature level at the thermocouple sensor reaches 700 degrees F, the system must shut down, closing all gas control valves (stopping all fire and smoke) and ventilating the fuselage for a minimum of 30 seconds after the temperature fall below 500 degrees F. | M
5.11 | Temperature Monitoring: Appropriate malfunction alert must be indicated on the control panel. | M
5.12 | Pilot Flame Status: Pilot Flame Status Monitoring: The burner head design must comply with NFPA 86. | M
5.13 | Pilot Flame Status Monitoring: Ignition sensor system must positively verify the presence of an adequate ignition source at the point where main burner ignition occurs. | M
5.14 | Pilot Flame Status Monitoring: Safe ignition of propane must be accomplished by using a proven pilot flame ignition source & pilot confirm system. | M
5.15 | Pilot Flame Status Monitoring: The pilot confirmation system must be a Kromschoder IFD 258 or equivalent. | M
5.16 | Pilot Flame Status Monitoring: The system must prevent pilot gas valves from opening in absence of an ignition source, and further prevent propane from being delivered to the main flame burners until the presence of a STABLE pilot flame has been established and confirmed. | M
5.17 | Pilot Flame Status Monitoring: All pilot flames, both interior and exterior to the aircraft mockup, shall be monitored as described here in (or alternative method previously approved by NATO AHJ). | M
5.18 | Hardware Malfunction: Hardware functions such as gas supply valve position and pilot flame status must be monitored by the control system; If these or the status of any other monitored conditions is incorrect, the trainer must automatically and immediately shut down, and operation must be disabled until the fault condition is corrected. | M
5.19 | Exhaust Ventilation System and Monitoring: The live fire trainer must have a ventilation system designed to remove excess heat, combustion byproducts, smoke, and unburned gas from fuselage. | M
5.20. | The ventilation system must consist of a high temperature exhaust fan, and intake louvers designed to fully purge the fuselage in accordance with NFPA 1402. | M
5.21 | The live fire training system must control the operation and monitor the airflow of the ventilation system in the fuselage. | M
5.22 | The ventilation system must be activated and run at full speed during the following conditions: 1) To purge the trainer prior to operation 2) With alarm level gas concentration or temperature alarm 3) With any automatic or manual emergency shutdown | M
5.23 | The ventilation system must continue to operate until the emergency condition has been corrected. | M
5.24 | Combustion Air System Monitoring: Sufficient combustion air must be supplied to the fuselage to provide an adequate air supply to the burner elements to ensure reliable combustion of the main flame gas source. | M
5.25 | Combustion Air System Monitoring: A sensor must confirm airflow. | M
5.26 | Combustion Air System Monitoring: Upon loss of the combustion air confirmation signal, the fireplace flame and smoke must shut down. | M
5.27 | Combustion Air System Monitoring: Appropriate malfunction alert must be indicated on the control panel. | M
5.28 | Combustion Air System Monitoring: The use of combustion air blower must ensure that there is always the adequate air supply for ignition of the main flame reducing possibility for buildup of gas. | M
5.29 | Combustion Air System Monitoring: Combustion air blower operation must be confirmed and interlocked with the safety system as required by NFPA 86. | M
5.30. | Emergency Shut-down: A hard-wired emergency shutdown (E-Stop) circuit must be provided for the trainer operating independently of the control system. | M
5.31 | Emergency Shut-down: Shutdown push buttons must be located in the control console and near each trainer entry door. | M
5.32 | Emergency Shut-down: The E-STOP button must cause all burner control valves to close, smoke productions to stop, and ventilation fans to run at maximum until safe operating conditions have been established and the E-STOP is manually reset. | M
5.33 | Power loss Automatic Shut Down: a) Fail-safe electrically operated valves must be used for propane vapor distribution b) The valves must close in less than one (1) second when de-energized c) If the computer monitoring system detects an unsafe condition, or the emergency shutdown system is activated or a loss of power occurs, the Fail Safe Valves must close and this action must stop all vapor propane distribution. | M
5.34 | Operator Controls: The mobile aircraft fire trainer must provide the means for a single operator to control all flame locations throughout the devices from a single location. | M
5.35 | Operator Controls: The mobile aircraft fire trainer must be equipped with operator controls that are sufficiently remote from the aircraft mockup as to remain outside of the firefighting activity and apparatus, while being close enough to observe tactical, safety, and training procedures. | M
5.36 | Operator Controls: The controls shall provide the means to individually select fires, to select all fire locations simultaneously, or select a combination (mix) of individual fire on the mockup. | M
5.37 | Operator Controls: The mobile aircraft fire trainer shall provide the means for the operator to extinguish all flames from a central location with a single action. | M
5.38 | Operator Controls: the mobile aircraft fire trainer shall be equipped with means such as a "dead man" switch to immediately shutdown the entire system upon release of the switch. The switch shall be required to remain depressed for the entire fire evolution. | M
5.39 | Operator Controls: When any safety switch is activated, all training fires and smoke must be immediately shut down and ventilation system shall be activated. | M
6 | Part 6: System Specifications (Operations)
6.01 | Operations: All systems and components must operate to the following standard: a. 20-100F (Out-door operations); b. -20-120F (storage); c. Compartment Operations: 32-100F; d. -20-120F (storage); e. Humidity from 0-100 percent; f. Minimum Gas Supply: 250Ils propane cylinder; g. Minimum Electrical Power Supply: 1). 240 VAC, 4-wire grounded; 2) Single Phase; 3) 60 Amps; 4) 60 Hz. | M
7 | Part 7: Flame Generation
7.01 | Flame Generation: Each training fire must be furnished with a flame generation system that shall include all components necessary to: a) Initiate and maintain a pilot for ignition of main flame, main flame burner elements within the fire trainer to distribute gas to produce flames b) Control valves to adjust gas flow to the main flame elements c) Interlocks with the trainer's safety systems | M
7.02 | The flame generation control system must include a separate automatic shut off valve interlocked to the trainer's safety systems to stop gas flow during any emergency shutdown situation or on loss of electrical power. | M
8 | Part 8: Trainer Components - Fuselage Mock-up (Will contain the following)
8.01 | Must have gas detection sensor - Dual Channel. | M
8.02 | Must have Smoke port. | M
8.03 | Must have burn-room temperature sensor. | M
8.04 | Heat shield system: The training compartment must be lined with weathered steel to protect the exterior walls from exposure to direct flames and damaging heat. | M
8.05 | Must have hinged passenger entrances (one port side, one on the left side, and one emergency entrance over a wing) with operable latches that simulate typical aircraft latches to hold the door closed. Entrances must also have operable latches that retain the doors in the "open" position. | M
8.06 | Must have a hinged cargo door/ramp aft | M
8.07 | Must have removable passenger seats provided on both sides of a center aisle. | M
8.08 | The trainer must provide the means to rearrange the passenger seats in a row configurations with their back against the fuselage on both sides of the aircraft's interior. | M
8.09 | Must have a sacrificial access panel for forced entry training. | M
8.10. | Panels must be 22" to 24" wide and 46" to 48" high. | M
8.11 | The location of the panel shall be clearly defined on the aircraft's exterior and accessible from the ground level. | M
8.12 | Once the panel has been destroyed, the panel must be easily removable so that new panel can be put in its place. | M
8.13 | The aircraft mockup must be reinforced around the sacrificial panel in anticipation of coming into accidental contact with forcible entry and rescue tools. | M
8.14 | Must have a simulated, hinged battery compartment installed in close proximity to the cockpit area. | M
8.15 | Must have National Fire Protection Association (NFPA) compliant gas-fueled, fire generation systems. | M
8.16 | Must have high temperature rated ventilation fan and monitoring system. | M
8.17 | Training floor must be fabricated of 3/16" stainless steel checker plate comes with drain holes. | M
8.18 | Emergency stop switches; must be located near each fuselage entrance and on the control console | M
9 | Part 9: Low Wing Component (Minimum Requirement)
9.01 | The low wing mockup must be located on the port side, 3'-4' from ground level. | M
9.02 | Low level engine mockup must be positioned 3'-4' from ground level. | M
9.03 | Must have low wing engine training fire. | M
9.04 | Must have landing gear mockup. | M
10 | Part 10: Lifting Winches
10.01 | The lifting winches must be used to lift and lower: a) The low wing structure b) The rear cargo gate | M
11 | Part 11: Stairs
11.01 | Two (2) entry stairs must be provided. | M
12 | Part 12: Power Generator
12.01 | Electric Generator: Must be gasoline fueled, minimum 12-15kw portable generator. | M
13 | Part 13: Fire Mock up
13.01 | All training fires must be designed for safe operation. | M
13.02 | The control system must allow all training exercises to be concurrently selected and initiated by the operator using the control panel located at the control station. | M
13.03 | The operator must be able to immediately stop any exercise should the need arise. | M
13.04 | The operator must, through radio communications, control fire operations in response to instruction from the instructor/safety officer at the mockup. | M
13.05 | The instruction/safety officer must enable fire operations using a "dead man" function switch. | M
13.06 | Cockpit Fires: The cockpit fire must provide training in the control and extinguishments of a Class C, electronic equipment. | M
13.07 | Cockpit Fires: The fire must be located in a flight console mockup between the cockpit seats. | M
13.08 | Cockpit Fires: The fire must be individually selectable. | M
13.09 | Passenger Fires: The passenger fire must provide training in the control and extinguishments of a Class A, passenger seat fire in the passenger area. | M
13.10. | Passenger Fires: The fire must be located under the seats. | M
13.11 | Passenger Fires: The fire must be individually selectable. | M
13.12 | Engine #1 (Low Wing): The wing engine fire must be designed to provide training in control and extinguishments of fire in turbofan engine that occur both when the engine is running and when the engine has been shut down. | M
13.13 | Engine #1 (Low Wing): The wing engine mockup must be located at the wing tip, left side of the fuselage. | M
13.14 | Engine #1 (Low Wing): The fire must be independently exercisable. | M
13.15 | Engine #1 (Low Wing): The length of the torching type running engine flame and lazy non-running engine flame must be operated from a switch at the control panel. | M
13.16 | Engine #1 (Low Wing): The running engine fire must provide flames at least 10' in length. | M
13.17 | Engine #1 (Low Wing): The engine must be equipped with a simulated air intake/turbine cowling to provide for realism. | M
13.18 | Engine #1 (Low Wing): The simulated cowling must provide the means to drain a steady stream of water directed by firefighters | M
13.19 | Fuselage Fire: The Fuselage fire must be designed to provide training in control and extinguishment of a fire on the exterior of the fuselage. | M
13.20. | Landing Gear Fire #1 (Low Wing): The landing gear fire must be designed to provide training in extinguishments of fires that occur if brakes are not properly cooled. | M
13.21 | Landing Gear Fire #1 (Low Wing): The landing gear mockup structure must be located under the aircraft mockup's wing and must be configured as a dual wheel assembly. | M
13.22 | Landing Gear Fire #1 (Low Wing): Each wheel mockup must be fabricated of Cor-Ten steel and must measure approximately 20"-22" in diameter and 10"-12" wide with cylindrically shaped representations of brakes from which flame shall emanate. | M
13.23 | Landing Gear Fire #1 (Low Wing): The fire must be individually selectable and operated from switches at the control panel. | M
13.24 | 3D Fuel Leak Fire: The three dimensional fuel leak fire must consist of a representation of an ignited fuel leak from the low wing engine #1 mockup leading to a fuel spill fire on the ground to the rear of the engine. | M
13.25 | 3D Fuel Leak Fire: The fire must be selectable to run in conjunction with the non-running wing engine fire. | M
13.26 | 3D Fuel Leak Fire: The fuel leak representation must produce a cascade fire falling a minimum of three feet below the engine into the fuel spill. | M
13.27 | 3D Fuel Leak Fire: The fuel spill fire must consist of a 2' to 2.5' by 2.5' to 3' foot burn area. | M
13.28 | 3D Fuel Leak Fire: The fire must engulf the fuel spill area. | M
13.29 | 3D Fuel Leak Fire: The fire must produce flames up to 6'-8' in height. | M
13.30. | 3D Fuel Leak Fire: The fire must be controlled by switches at the control panel. | M
13.08 | Cargo Fire: The Cargo fire must be designed to provide training in the control and extinguishment of a fire that has occurred in the cargo area of an aircraft. | M
13.09 | APU Fire: The APU fire must be designed to provide training in control and extinguishments of a fire that has occurred in an Auxiliary Power Unit on an aircraft. The flames must be emitted from an exhaust nozzle on the left side of the aircraft. | M
| APU Fire: The flames must be emitted from an exhaust nozzle on the left side of the aircraft. | M
13.1 | Fuel Spill: The Fuel Spill fire must be designed to provide training in control and extinguishments of a fire that has occurred as a result of a fuel spill. | M
14 | Part 14: Control Consol
14.01 | A control console must enable the operator to control the live fire training system, including functions such as initiation of pilot flames, main flame height control, activation of flashover-rollover effect, control of smoke generation, and control of ventilation system. | M
14.02 | The control consoles rotary knobs must be illuminated. | M
14.03 | Each knob must be color coded for a specific function. | M
14.04 | Illumination state (i.e. solid, flashing, or off) of each rotary knob must identify the status of each function. | M
14.05 | A wireless controller must be included that likewise shall enable the operator to control the live fire training system, including functions such initiation of pilot flames, main flame height control, optional control of smoke generation, and control of the ventilation system. | M
14.06 | The operator shall be able to initiate the pilot flame and the smoke system at the control panels. When a pilot flame is confirmed the operator is clear to control ignition of the front and rear fires using the handheld control unit. | M
14.07 | Flame Generation: Each training fire must be furnished with a flame generation system that shall include all components necessary to: a) Initiate and maintain a pilot for ignition of main flame, main flame burner elements within the fire trainer to distribute gas to produce flames. b) Control valves to adjust gas flow to the main flame elements. c) Interlocks with the trainer's safety systems. | M
14.08 | The flame generation control system must include a separate automatic shut off valve interlocked to the trainer's safety systems to stop gas flow during any emergency shutdown situation or on loss of electrical power. Main flame shall be extinguishable ONLY by the trainer operator and NOT by application of agent. | M
15 | Part 15: Post Delivery Training of Military Fire Fighters
15.01 | Contractor must provide training to end users after delivery of the MARFFS. | M
15.02 | Training must consist of simulator set, tear down, limitations, safety and basic user maintenance. | M
16 | Part 16: Annual Maintenance
16.01 | The contractor must provide detailed annual maintenance on the simulator at no cost to DND. | M
17 | Part 17: Routine Maintenance
17.01 | DND will be responsible for routine wear and tear type maintenance issues. | M
17.02 | Non-routine wear and tear maintenance issues will be the responsibility of the manufacturer. | M
18 | Part 18: Delivery, Acceptance, Return and Inspection Requirements
18.01 | Delivery and inspection will be carried out at CFB Greenwood, Nova Scotia by the Royal Canadian Air Force (RCAF) Fire Marshal. | M
18.02 | Acceptance of the MARFFS will be done by the RCAF Fire Marshall upon demonstration of the unit being fully operational and the required training of the unit completed. | M
18.03 | A predelivery inspection at the bidders plant will take place by the RCAF Fire Marshal prior to the unit being delivered to CFB Greenwood. | M
18.04 | Initial company training for users will take place at Canadian Forces Base Greenwood, Nova Scotia. | M
18.05 | Upon completion of the lease term, the offerer will be fully responsible to remove the simulator from DND property. | M
18.06 | The offeror will be fully responsible for all cross border requirements, administrative procedures and transportation of the simulator. | M
19 | Part 19: General
19.01 | The contractor must identify the specific make and model offered and provide a complete Operator and Maintenance (O&M) manual and drawing set with the offer. | M
19.02 | The make and model offered must be previously approved by a NATO Country Fire Marshall (or equivalent) and that supporting documentation is provided with the offer. | M
19.03 | The make and model offered must be a type currently being leased in the marketplace. | M
19.04 | The contractor must provide a minimum of two (2) reference contact information of current lease customers. The lease customers must be for at least two (2) new stainless steel simulators delivered in the last 36 months, currently still in use. | M
19.05 | The contractor must have a minimum of five (5) years experience working with NATO Air Forces and provide testimonial documentation to prove. | M
19.06 | The offeror must be able to conduct business in Canada. | M